## Sheet1
REPLIES TO QUERIES Tender No. 05/2018 HVAC WORKS FOR INCUBATION CENTRE 12/6/2018
S NO | QUERY DESCRIPTION | REPLY
1 | Thickness of Insulation for MS Chilled water Pipes. | This is as per DSR item. 50 mm thick.
2 | Whether FCUs are specified with double skin or single skin ? | Single skin.
3 | Actuators and Two way Valves : ON/OFF ( Binary ) or Proportional ? | ON/OFF
b | : Pressure Independent Control Valve ( PICV ) or not ? | NA
4 | Thermostatic Control : Whether Digital or Manual ? | Manual
b | Whether with builtin sensor or remote sensor ? | Built in Sensor